## Annex A - ICT requirements
Features |  |  |  | ICT requirement |  | IEC references
|  |  |  | Requirement | Comment | IEC document reference |  |  | SCL impact
Nr | Sub-Nr | Feature | Feature Detail |  |  | Document | Reference | SCL example from IEC document | SCL 2007B4 + 6-100 2019B9 | SCL 2007C5 + 6-100 2019C1
A |  | Minimal Requirements for Top Down Engineering
1 | 1 | Namespace | Support SCL 2007B4 (or newer) | capable of importing files in this namespace and exporting ICD/IID in this namespace | minimal requirement to support top-down engineering SCL extensions from IEC61850-6-100 | IEC 61850-6 ed2.1
1 | 1 | Namespace | Support SCL extension 6-100 2019B9 (in combination with SCL 2007B4) | capable of importing files in this namespace and exporting ICD/IID in this namespace |  | TR IEC 61850-90-30 ed1.0
1 | 2 | Compliance with top-down engineering process | SSD/ISD from SST to ICT; process ICD/IID from ICT to SCT | the ICT needs to be capable of importing an SSD/ISD, importing and interpreting the process section and exporting a process ICD/IID for each specified S-IED |  | TR IEC 61850-90-30 ed1.0 | 16.3 + 16.4 + 16.6
1 | 3 | Mapping of LNode to LN | mapping specification LNode to IED LN 1 LNode to 1 LN | Updating the process section LNode data model with an LN data model from the IED | see PIU_IMP.icd | TR IEC 61850-90-30 ed1.0 | table 42 + 16.4.5 | TR IEC 61850-90-30 Figure 87
B |  | Supplementary Requirements: Namespace and uuid
1 | 1 | Namespace | Support SCL 2007C5 (or newer) | capable of importing files in this namespace and exporting ICD/IID in this namespace |  | IEC 61850-6 ed2.2 or newer
1 | 2 | Namespace | Support SCL extension 6-100 2019C1 (in combination with SCL 2007C5) or newer | capable of importing files in this namespace and exporting ICD/IID in this namespace |  | TR IEC 61850-90-30 ed1.0
1 | 3 | UUID | Creating uuid attributes for IED elements | Adding UUID attributes to IED elements like LN and ExtRef/ExtCtrl | see PIU_IMP.icd - this allows to document mapping of SourceRef to ExtRef and DO- and DA-mapping using uuid references | IEC 61850-6 ed2.2 or newer | 8.5.6 |  | not possible
B |  | Supplementary Requirements: Specification Traceability |  | I require full traceability between SCL files (sources and templates) - I want to trace which files (SSD/ISD/SCD)(including their version information) are used to specify and configure an IED
2 | 1 | Specification Traceability | Using SSD/ISD reference in ICD/IID - source file definition for traceability of specification source | Placing the SSD/ISD reference in the Header (SourceFiles) and IED (IedSourceFiles) using uuid | see PIU.isd and PIU_IMP.icd (Header SourceFiles and IEDSourceFiles) | IEC 61850-6 ed2.2 TR IEC61850-90-30 | IEC 61850-6 9.3.2 TR IEC61850-90-30 17.4 | IEC_61850-6.2023.SCL.2007C5.full\Annex D - SCL example.scd | not possible | using (IED)SourceFiles
B |  | Supplementary Requirement: Physical Allocation - S-IED |  | I want to specify an IED datamodel and IED services using the S-IED element of an SSD/ISD
3 | 1 | Import of an SSD or ISD file with S-IED | Using S-IED to specify IED data models and using Services element to specify required services | Understanding the S-IED services to compare them with the IED services to find/select only compatible IEDs | see PIU.isd | TR IEC 61850-90-30 ed1.0 | Annex B | IEC_61850-90-30.SSD.2024A2.full\P21 SCL examples\ISD
B |  | Supplementary Requirement: Physical Allocation |  | I assign functions to a single AllocationRole (corresponding to option 1 of the document)
3 | 2 | Import of an SSD or ISD file without S-IED, with AllocationRole | Using AllocationRole to specify and constraint physical allocation of Lnodes (1 function to 1 AllocationRole - option 1) | Identifying specification based on AllocationRole function references , and not based on S-IED data model | see ICT_REQ.ssd | TR IEC 61850-90-30 ed1.0 | 11.4 | IEC_61850-90-30.SSD.2024A2.full\IEC 61850-90-30 examples.ssd
B |  | Supplementary Requirement: Physical Allocation |  | for one or more devices, I specify a general allocation role, and let the IED supplier decide how to implement it in one or several IEDs (corresponding to option 2 of the document)
3 | 3 | Import of an SSD or ISD file without S-IED, with AllocationRole | Using AllocationRole to specify and constraint physical allocation of Lnodes (1 Function to N AllocationRoles - option 2) | Identifying specification based on AllocationRole function references , and not based on S-IED data model | see ICT_REQ.ssd | TR IEC 61850-90-30 ed1.0 | 11.4 | IEC_61850-90-30.SSD.2024A2.full\IEC 61850-90-30 examples.ssd
B |  | Supplementary Requirement: Physical Allocation |  | I want to give full flexibility to the IED supplier to assign specified LNodes to the real IED
3 | 4 | Import of an SSD or ISD file without S-IED and AllocationRole | Giving IED supplier full flexibility in assigning LNodes to devices |  |  | TR IEC 61850-90-30 ed1.0
B |  | Supplementary Requirement: Complex mapping scenarios |  | I accept flexible mapping of my specification (LNode to LN being 1 to 1 or 1 to N or N to 1)
4 | 1 | Mapping of LNode to LN | mapping specification LNode to IED LN 1 LNode to N LNs or N LNodes to 1 LN | Resetting LNode iedName to "none" and documenting data model mapping through individual DO/DA mapping using mappedDoName (at DOS/SDS) and mappedDaName (at DAS) |  | TR IEC 61850-90-30 ed1.0 | table 42 + 16.4.5 | TR IEC 61850-90-30 Figure 101 | using mappedDoName (at DOS/SDS) full path and mappedDaName (at DAS) full path creating DOS/SDS/DAS elements if necessary | using LN uuid and mappedDoName (at DOS/SDS) internal path and mappedDaName (at DAS) internal path creating DOS/SDS/DAS elements if necessary
B |  | Supplementary Requirement: Creating dataflow placeholders |  | I will specify the dataflow to send and receive by an IED and expect to use tailored later binding elements from the process ICD/IID to configure IED dataflow in the SCT
5 | 1 | For Goose, Sampled Values and Reporting | Mapping SourceRef to ExtRef | Placing the ExtRef reference in the specified SourceRef | see PIU_IMP.icd | TR IEC 61850-90-30 ed1.0 | table 6 (extRefAddr format) + table 42 + 16.4.5 | TR IEC 61850-90-30 Figure 15 | extRefAddr attribute of SourceRef | extRefUuid attribute of SourceRef
5 | 2 | For MMS control | Mapping ControlRef to ExtCtrl (only for MMS client specification) | Placing the ExtCtrl reference in the specified ControlRef |  | TR IEC 61850-90-30 ed1.0 | table 8 (extCtrlAddr format) + table 42 + 16.4.5 | TR IEC 61850-90-30 Figure 15 | ExtCtrl is not supported by SCL 2007B4 | extCtrlUuid attribute of ControlRef
B |  | Supplementary Requirement: Value Specification |  | I want to specify values for IED configuration (e.g. configuration values, settings, labels)
8 | 1 | Value specification | Mapping DOS/SDS/DAS to DOI/SDI/DAI | creating DOI/SDI/DAI in IED data model - implementing values from LNode DAS |  | TR IEC 61850-90-30 ed1.0 | 16.4.2 + 16.4.3 + table 42 |  | Labels not supported | labels copied to IED section DOI/SDI/DAI
B |  | Supplementary Requirement: Behavior Description Implementation |  | I use BehaviorDescription elements in my SSD/ISD to specify logical behavior and expect the IED supplier to document any implementation detail/deviation from my specification via a new BehaviorDescription attached to his ICD/IID response
9 | 1 | BehaviorDescription implementation | Documenting deviating IED behavior compared to specification | Adding a new BehaviorDescription element to the process ICD/IID process section with BehaviorReference of the specified BehaviorDescription. The new BehaviorDescription documents how the specified BehaviorDescription is implemented by the IED (details and/or deviations) | alternatively, a third party tool can be used to add the additional BehaviorDescription element outside the ICT | TR IEC 61850-90-30 ed1.0 | 13 + 16.4.5.2.2