| Requirements for IED Configuration Tools in Top-Down Engineering - Specification Process |  |  |
| --- | --- | --- |
| Specification |  |  |
| Virtual Substations |  |  |
| Summary |  | This document describes the requirements for the IED Configuration Tool with regards to the interface with the System Engineering Tool for exchange of specification and IED capabilities |  |
| Version |  | v0 |  |
| Date |  | Date of the current version |  |
| Status |  | Draft | Final |

Document creation and distribution

| Author | Thomas Sterckx |
| --- | --- |
| Function | Expert |
| File location | https://eliagroup.sharepoint.com/sites/Project/VirtualSubstations/Shared Documents/30. Industry Steering/07. Common Statements/01. ICT/Requirements for IED Configuration Tools in a top-down engineering specification process.docx |
| Distribution | Please enter the names of the persons who will receive the document |

Approval

| Version | Date | Name | Function | Signature |
| --- | --- | --- | --- | --- |
| Last version number | Approval date | First name + name | Function |  |

Previous versions

| Version | Date | Author | Summary of changes |
| --- | --- | --- | --- |
| Version number | Version date | First name + name | Description of changes |

Related documents

| Document ID | Document title |
| --- | --- |
| Document ID | Document title |
| Document ID | Document title |
| Document ID | Document title |

## Contents

1.	Purpose of this document	4

2.	Context	4

2.1	Introduction	4

2.2	Industry steering references	4

2.3	IEC 61850 reference documents	5

2.4	Top-down engineering and the role of the ICT	5

2.5	Demo system	7

2.6	Detailed process	10

2.6.1	Interaction between SSD/ISD and process ICD/IID	10

3.	Requirements	11

3.1	Introduction – The User Profile	11

3.2	Minimal ICT requirements	11

3.2.1	Namespace	11

3.2.2	Compliance with top-down engineering process	11

3.2.3	Mapping of LNode to LN	11

3.3	Supplementary ICT requirements	11

3.3.1	Namespace and UUID	11

3.3.2	Specification traceability	12

3.3.3	Physical Allocation	12

3.3.4	Complex mapping scenarios	14

3.3.5	Creating dataflow placeholders	14

3.3.6	Value specification	14

3.3.7	Behavior Description implementation	15

4.	Elia’s user profile – Supplementary requirements	16

5.	Annexes	17

5.1	Annex A: Requirements table	17

5.2	Annex B: demo SCL files	17

Figure 1 - exchange between system engineering tools and IED configuration tools	4

Figure 2 - Engineering process as described in TR IEC 61850-90-30	6

Figure 3 - Focus elements of this document	6

Figure 4 - Exchange between user and IED supplier	7

Figure 5 - demo system function tree structure (template)	8

Figure 6 – Example of a specified system vs a vendor IED implementation	9

Figure 8 – Interaction process tree	10

Figure 9 – SCL file reference process	12

Figure 10 – Trip from CB interface LNode to binary output LNode	13

Figure 11 – AllocationRole option 1	13

Figure 12 – AllocationRole option 2	14

Figure 13 – Tool interaction related to behavior description	15

Requirements for IED Configuration Tools in  Top-down Engineering  - Specification Process

Purpose of this document

This document is oriented towards IED Configuration Tool suppliers and provides a formalized set of requirements for how ICTs must interpret IEC 61850 system specifications and respond with compliant process ICD/IID files in a top-down engineering environment. It defines both mandatory baseline capabilities and optional supplementary features depending on the user’s engineering philosophy, with Elia’s own profile serving as a concrete example.

The scope of this document is limited to requirements related to import of an SCL user specification (SSD or ISD) and creation of a process ICD or IID response.

All details related to the engineering process and handling of SCL (substation configuration language) data are interpretations and clarifications of the content of the different IEC documents defined in 2.3. There are no additional requirements or specifications formulated in this document as it intends to follow the IEC 61850 standard completely.

Context

Introduction

Since the release of IEC 61850-6 edition 2.1 in 2018 important initiatives were started in the industry and at standardization level to enable top-down engineering processes for IEC 61850 engineering. This resulted in a series of publications and proof of concept projects listed hereunder.

The biggest accomplishment of these developments is the creation of a framework that allows the exchange of a formal machine processable file format between system engineering tools and the IED configuration tool.

Figure 1 - exchange between system engineering tools and IED configuration tools

The details of this exchange are described in TR IEC 61850-90-30. This document focuses on the requirements for the ICT (IED Configuration Tool) necessary to support this exchange.

Industry steering references

- Engineering common vision: IEC61850 Engineering Process Common Vision

- Proof of concept executed by Elia in 2023: Webinar - IEC 61850 Engineering Process Common Vision - YouTube

- Osmose engineering process refinement published in 2021: OSMOSE releases an enhanced engineering process for IEC61850 standard – Osmose

IEC 61850 reference documents

- IEC 61850-6:2009/AMD2:2024 - Communication networks and systems for power utility automation - Part 6: Configuration description language for communication in electrical substations related to IEDs.

  - Code component SCL namespace version 2007C5

- TR IEC 61850-90-30:2025 - Communication networks and systems for power utility automation - Part 90-30: IEC 61850 Function Modelling in SCL.

- TR IEC 61850-7-6:2024 - Communication networks and systems for power utility automation - Part 7-6: Guideline for definition of Basic Application Profiles (BAPs) using IEC 61850

- Common code component from TR IEC 61850-90-30 and TR IEC 61850-7-6: SCL extension namespace 6-100:2019C1

This document has references to all of the above documents, it is highly recommended readers have their own copy of these.

Top-down engineering and the role of the ICT

The term “Top-Down Engineering” is being wildly used within the industry to describe many variants of the IEC 61850 engineering process. This document intends to provide a clear definition of how it should be interpretated within the context of this document. Top-Down Engineering is defined by a series of conditions

- A user provides a standardized, machine-processable format the specification for a system, containing

  - Data model specification

  - Dataflow specification

  - Specification of values for configuration of the IED

  - Physical allocation constraints

A user can create this specification using a third-party System Specification Tool

- An IED supplier is able to provide in a machine processable format (using their IED Configuration Tool) the capabilities of the offered devices and the mapping to the original specification

  - Data model mapping

  - Mapping of specified dataflow to dataflow configuration placeholders

  - Configuring specified values in the IED

- A user can integrate this response from the IED supplier in his system using a System Configuration Tool, and finalize the configuration of the system, configuring dataflow and values of these IEDs

- An IED Configuration Tool imports the system configuration and uses it to configure the IED’s dataflow and parameters

This description is demonstrated  by TR IEC 61850-90-30 and shown below

Figure 2 - Engineering process as described in TR IEC 61850-90-30

The requirements described in this document focus on the 2 steps below

Figure 3 - Focus elements of this document

The expected exchange between user and IED supplier is the following

Figure 4 - Exchange between user and IED supplier

Please note that requirements for any tools at user side are out of scope of this document.

Demo system

To clarify different use cases a demo system is used. This allows the use of examples to explain and clarify certain concepts. The demo system describes the specification of a template system that takes the current measurement of a neuter point of a transformer and performs an overcurrent protection on it. It is split in 2 main functions, one for the protection IED, and one for the PIU IED. There is dataflow exchange configured to send the current measurement from the CT to the overcurrent protection function, and from the protection function over the trip function and circuit breaker interface to the PIU physical resources (conditioner + binary output). As defined by TR IEC 61850-90-30 a system specification template is defined by a system hierarchy with Substation, Voltage Level and Bay called “TEMPLATE” (as indicated in Figure 5 - demo system function tree structure (template)) to indicate that its purpose is a template.

Figure 5 - demo system function tree structure (template)

The implementation part however shows that it is not possible to implement the system as specified in the offered IEDs.

The PIU does not support the physical resource LNs and needs to model the conditioner and binary output as GAPC instances, and the goose subscription can only be received by an LLN0 of the IED.

Figure 6 – Example of a specified system vs a vendor IED implementation

As indicated in the image, attached to this document (5.2 Annex B: demo SCL files) are a series of files describing the system and demonstrating what the SCL output of the different engineering tools needs to look like.

Detailed process

To differentiate the different in- and outputs of the process a series of use cases are defined:

Figure 7 – Interaction process tree

Interaction between SSD/ISD and process ICD/IID

The expected content of the different files is described in several detailed tables of TR IEC 61850-90-30

- For ISD à table 41

- For Process ICD à table 42

- For Process IID à table 43

The general purpose of the process ICD/IID is to describe how the supplier’s IED maps to the specification.

To perform the mapping, the ICT requires interpretation of the process section of the received SSD/ISD file and, in case of an S-IED specification, also the services from the IED section of the S-IED.

The ICT then produces a process ICD/IID as a formal answer to the specification in which the mapping of the device is documented. Rules on how to document this mapping are described in the above-mentioned tables and in TR IEC 61850-90-30 part “16.4.5.2 Different non-comply scenarios of the process ICD/IID”.

Requirements

Introduction – The User Profile

To create ICT requirements tailored to the needs of each user, this document is set up in a way that it distinguishes between

- Minimal requirements valid for all IED suppliers

- Supplementary requirements than can be selected based on each user’s needs

The unique combination of supplementary requirements a user selects is called a user profile. The following chapters give an overview of all requirements, which are explained in more detail in 5.1 Annex A: Requirements table

Each chapter corresponds to an item in the Annex.

Minimal ICT requirements

Namespace

A minimum to execute top-down engineering process is the combination of

- SCL namespace 2007B4 (IEC 61850-6 ed2.1)

- 6-100 namespace 2019B9

It supports the creation of a concept and system specification containing data models, dataflow and values. However newer namespaces enable additional features like traceability using uuid concepts, and documentation of labels.

Compliance with top-down engineering process

As a minimum, the ICT needs to support the expected file interface between the user and IED supplier.

Mapping of LNode to LN

The user will provide the expected data model for LNodes to the IED supplier using an SSD or ISD. The IED supplier is expected to provide a formal answer to the specification, using process ICD/IID (according Figure 3 - Focus elements of this document). In the file, the IED supplier needs to document how the specified LNodes are mapped to the proposed IED.

The ICT needs to be capable of supporting the most basic mapping use case of a required data model to the data model of the proposed IED (1 to 1 LNode/LN mapping).

In case a perfect 1 to 1 mapping between LNode and LN is not possible (1 to N or N to 1 (see TR IEC 61850-90-30 part “16.4.5.2 Different non-comply scenarios of the process ICD/IID”)) additional features are required (see 3.3.4 Specification of IED allocation boundaries).

IED suppliers need to be aware that the required LD/LN structure may differ between users, depending on each user’s context and needs. The example below demonstrates this with an example of a specification and 4 different ways that users may map them to a logical device structure.

Figure 8 - Specification example of a function with 3 subfunctions

Figure 9 - 4 ways users may decide to map the LNodes to an IED LD structure

Supplementary ICT requirements

Namespace and UUID

To enable maximal use of new concepts like uuid, traceability and labels the following namespace combination needs to be supported

- SCL namespace 2007C5 or newer (IEC 61850-6 ed2.2)

- 6-100 namespace 2019C1

Specification traceability

To trace the reference and version of the specification file (SSD/ISD), the process ICD/IID needs to store these in the process ICD/IID file according to the rule from TR IEC61850-90-30 chapter 17.4.

Figure 10 – SCL file reference process

Physical Allocation

A user may have requirements related to allocation of LNodes to IEDs. There are 2 ways to describe these in SCL specification using an S-IED or AllocationRole. The following table gives an overview of the different options users have for specifying how the specified LNodes need to be allocated to IEDs.

| User SCL Specification content / property | S-IED | AllocationRole | LNodes not assigned to S-IED or AllocationRole |
| --- | --- | --- | --- |
| LNode.iedName | iedName filled in (TEMPLATE or project specific) | iedName = "none" | iedName = "none" |
| Format | SSD or ISD | SSD only | SSD only |
| Contains IED element | yes | no | no |
| Assigning an LNode | to 1 IED only | option to provide allocation flexibility | no allocation constraints given |
| Specify minimal IED services | yes | not possible | not possible |

Table 1 – Physical allocation specification overview

- In case an S-IED is used, the data model boundaries of the IED are clear and there is no ambiguity possible.

  - The use of S-IED enables the possibility to document requirements for the IED services that proposed IEDs need to support (for ex. Minimal amount of Goose messages the IED can publish/subscribe to), as specified in TR IEC61850-90-30 Annex B. This document also contains an SCL example “PIU.isd” in Annex B: demo SCL files.

- When LNodes are not assigned to an S-IED, nor to an AllocationRole, this indicates that the user has no physical allocation constraints and provides full flexibility to the IED supplier.

- When LNodes are not assigned to an S-IED, but to an AllocationRole, this means the user

  - Wants to provide allocation flexibility to the IED supplier and/or

  - Does not want to specify any minimal IED services

More details on the AllocationRole are given in TR IEC 61850-90-30 part 11.4.

The example below shows the different allocation possibilities using AllocationRole. Represented in the figure hereunder is a specified system consisting of 3 LNodes representing the tripping of a circuit breaker from the circuit breaker interface XCBR LNode to the binary output LPDO LNode, going over the conditioning LNode.

Figure 11 – Trip from CB interface LNode to binary output LNode

AllocationRole - Option 1: user knows exactly where these LNodes need to be implemented. The user will assign the functions to only 1 AllocationRole. This option is represented in the image below.

Figure 12 – AllocationRole option 1

This option is close to specifying physical allocation using S-IED, but lacks the specification of minimal IED services (see 3.3.3 IED Services).

AllocationRole - Option 2: the user wants to provide flexibility to IED suppliers to allow integration of the XCBR in the BCU (Bay Controlling Unit) or in the PIU (Process Interface Unit).

Figure 13 – AllocationRole option 2

This figure shows also that the LCBO and LPDO LNodes cannot be implemented by a device performing BCU role, but only by a PIU.

Option 3: the user does not specify any allocation constraints, and provides full flexibility to the IED supplier

Remark: Limits of the modelling - what is not specified:

- If the user accepts a single IED performing a grouped BCU and PIU.

- If the user accepts multiple IEDs splitting the tasks of an AllocationRole (for ex. 2 PIU IEDs, one with LCBO and one with LPDO)

This information needs to be exchanged between user and IED supplier by another medium.

Complex mapping scenarios

Users can decide if only perfectly matched specifications are allowed or if IED suppliers can use a workaround to fulfill the data model requirement (see TR IEC 61850-90-30 part “16.4.5.2 Different non-comply scenarios of the process ICD/IID”).

When a proposed IED is implementing a specified LNode with a 1 to N or N to 1 relationship (and not a perfect 1 to 1 match), then the ICT needs to apply specific rules to document this type of mapping.

Creating dataflow placeholders

Within a system specification, users can decide to specify dataflow between LNodes, and expect IED suppliers to foresee dataflow receiving placeholders in the process ICD/IID which

- Match the dataflow specification (mapping an ExtRef to a SourceRef and an ExtCtrl to a ControlRef)

- Will be used by the SCT (System Configuration Tool) to implement the specified dataflow in the real IEDs (see Figure 2 - Engineering process as described in TR IEC 61850-90-30)

Value specification

SCL specification allows users to specify a series of values:

- Setting values (protection, automation settings)

- Configuration values (for ex. Control model)

For this, the concept of DOS/SDS/DAS is used to specify the values inside the LNode of the SSD/ISD. As described in TR IEC 61850-90-30 tables 42 and 43, it is expected that the process ICD/IID takes over these values as DOI/SDI/DAI in the IED data model of the proposed IED.

Behavior Description implementation

With the possibility to attach external files to an SCL specification using the BehaviorDescription element (see TR IEC 61850-90-30 chapter 13) users can specify the expected behavior of a specified system. Optionally they can express this in a standardized language for logic based on IEC 61131-3.

Figure 14 – Tool interaction related to behavior description

Users may require the IED supplier to document how the specification is implemented in the proposed IED. IED suppliers can do this by adding an additional behavior description to the process ICD/IID which references the original behavior description specification.

TR IEC 61850-90-30 does not restrict the format of the added behavior description file which should be part of a discussion between user and IED supplier. The usage of IEC 61131-3 to represent the required logical behavior does not mandate the implementation of this behavior using a programable logic in the vendor IED. This behavior specification may not be done with the deployment in mind. This is the discussion between the user and the vendor which will define how the vendor must consider this IEC 61131-3 representation of the specified logical behavior.

Elia’s user profile – Supplementary requirements

| Features |  |  |  |
| --- | --- | --- | --- |
| Nr | Sub-Nr | Feature | Feature Detail | Elia User Profile |
| B |  | Supplementary Requirements: Namespace and uuid |  |  |
| 1 | 1 | Namespace | Support SCL 2007C5 (or newer) | YES |
| 1 | 2 | Namespace | Support SCL extension 6-100 2019C1 (in combination with SCL 2007C5) or newer | YES |
| 1 | 3 | UUID | Creating uuid attributes for IED elements | YES |
| B |  | Supplementary Requirements: Specification Traceability |  |  |
| 2 | 1 | Specification Traceability | Using SSD/ISD reference in ICD/IID - source file definition for traceability of specification source | YES |
| B |  | Supplementary Requirement: Physical Allocation - S-IED |  |  |
| 3 | 1 | Import of an SSD or ISD file with S-IED | Using S-IED to specify IED data models and using Services element to specify required services | YES |
| B |  | Supplementary Requirement: Physical Allocation |  |  |
| 3 | 2 | Import of an SSD or ISD file without S-IED, with AllocationRole | Using AllocationRole to specify and constraint physical allocation of Lnodes (1 function to 1 AllocationRole - option 1) | NO – IED specification always via S-IED (ISD file) |
| B |  | Supplementary Requirement: Physical Allocation |  |  |
| 3 | 3 | Import of an SSD or ISD file without S-IED, with AllocationRole | Using AllocationRole to specify and constraint physical allocation of Lnodes (1 Function to N AllocationRoles - option 2) | NO – IED specification always via S-IED (ISD file) |
| B |  | Supplementary Requirement: Physical Allocation |  |  |
| 3 | 4 | Import of an SSD or ISD file without S-IED and AllocationRole | Giving IED supplier full flexibility in assigning LNodes to devices | NO – IED specification always via S-IED (ISD file) |
| B |  | Supplementary Requirement: Complex mapping scenarios |  |  |
| 4 | 1 | Mapping of LNode to LN | mapping specification LNode to IED LN 1 LNode to N LNs or N LNodes to 1 LN | YES |
| B |  | Supplementary Requirement: Creating dataflow placeholders |  |  |
| 5 | 1 | For Goose, Sampled Values and Reporting | Mapping SourceRef to ExtRef | YES |
| 5 | 2 | For MMS control | Mapping ControlRef to ExtCtrl (only for MMS client specification) | YES |
| B |  | Supplementary Requirement: Value Specification |  |  |
| 8 | 1 | Value specification | Mapping DOS/SDS/DAS to DOI/SDI/DAI | YES – only data attributes with functional constraint CF (configuration) or SP (setting) |
| B |  | Supplementary Requirement: Behavior Description Implementation |  |  |
| 9 | 1 | BehaviorDescription implementation | Documenting deviating IED behavior compared to specification | YES - An additional Behavior Description is only required if implemented behavior differs from specified. IED suppliers may use 3th party tools to update the process ICD with the additional Behavior Description |

Table 2 – Elia user profile

Annexes

Annex A: Requirements table

Annex B: demo SCL files